| Month |  | System Name |  |
| --- | --- | --- | --- |
| Year |  | PWSID |  |

| TURBIDITY: Combined Filter Effluent (CFE) Turbidity Limit: 0.3 NTU in at least 95% of the monthly measurements reported (highest individual turbidity measurement determined in each 4 hour monitoring period) Maximum Turbidity Limit: 1 NTU at any time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - Total number of CFE filtered water turbidity measurements: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Total number of CFE filtered water turbidity measurements that are less than or equal to 0.349 NTU: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Percentage of turbidity measurements less than or equal to 0.349 NTU |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| (Row B/Row A*100) = _______/_______ * 100: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - If Row C is <95%, date and time reported to State: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Highest Turbidity for Month in NTU: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Record the date and turbidity value for any measurements exceeding 1.049 NTU: If none, enter “none” |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Date and Time |  | Turbidity, NTU |  |  | Date and Time Reported to State |  |  |  |  |  |  |  |  |
| - Individual Filter Effluent (IFE) Turbidity: Results/Additional Actions (If none, enter “none”) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Filter No. | Exceedance Condition* | Date and Time | Turbidity, NTU |  | Additional Actions** and Date and Time Reported to State |  |  |  |  |  |  |  |  |
| - IFE and CFE Monitoring and Recording: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Was each filter and CFE monitored continuously? |  |  |  |  |  |  | Yes |  | No |  |  |  |  |  |
| - Were measurements recorded every 15 minutes? |  |  |  |  |  |  | Yes |  | No |  |  |  |  |  |
| - Was there a failure of the continuous monitoring equipment? |  |  |  |  |  |  | Yes |  | No |  |  |  |  |  |
| Disinfection Performance Criteria at Point-of-Entry to Distribution: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Total number of disinfection residual measurements at point of entry |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Total number of disinfection residual measurements that are less than 0.5 mg/l free chlorine systems or 0.5 mg/l total chlorine for chloramine systems |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Days the Residual was < 0.5 mg/L free or < 0.5 mg/L total (If none, enter “none”) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Date and Time |  | Duration of Low Level (hrs.) |  |  | Date and Time Reported to State |  |  |  |  |  |  |  |  |
| I DECLARE UNDER PENALTY OF PERJURY THAT THE FOREGOING IS TRUE AND CORRECT. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Prepared by: |  |  | Date: |  |
| --- | --- | --- | --- | --- |
| Operator ID #: |  | Water Treatment Certification Level |  |  |
| Systems are required to send this Form, the Distribution Disinfectant Form, Maximum Residence Time and Additional Chlorine Residual Reports, IFE Data Sheet, and Daily Data Sheet to the OPH District/Regional Engineering Office within ten (10) days following the end of each calendar month (LAC 51:XII.311.A). |  |  |  |  |

Complete This Page If Applicable

Failure of Continuous Turbidity Monitoring Equipment

| Location of Continuous Turbidimeter (Example: CFE, IFE 2) | Date and Time the Failure Occurred | Date and Time Continuous Turbidimeter was returned to service |
| --- | --- | --- |

Surface Water Plant Out of Service

| Date and Time Treatment Plant Offline/Out of Service | Date and Time Treatment Plant Returned to Service/Online |
| --- | --- |

I DECLARE UNDER PENALTY OF PERJURY THAT THE FOREGOING IS TRUE AND CORRECT.

| Prepared by: |  |  | Date: |  |
| --- | --- | --- | --- | --- |
| Operator ID #: |  | Water Treatment Certification Level |  |  |

Instructions and Guidance for Properly Completing the Compliance Determination Form

TURBIDITY: Combined Filter Effluent (CFE) Turbidity limit with significant digits is 0.349 in at least 95% of monthly measurements reported. (LAC 51:XII.1115.C.1) Maximum turbidity limit at any time with significant digits is 1.49 (LAC 51:XII.C.2) Turbidity measurements are to be taken at the combined filter effluent prior to clearwell entry. If not possible, other monitoring locations/arrangements must be approved by OPH on a case-by-case basis as per LAC 51:XII.1135.A. Row D – Throughout the month if CFE measurements will result in non-compliance with the turbidity standard (less than 95% of the measurements are less than or equal to 0.349 NTU), notify the local regional/district office as soon as possible but no more than 48 hours of the non-compliance occurrence. Provide the date and time the State was notified. (LAC 51:XII.1133.B.1)

Row/Table F – For any CFE turbidity measurements exceeding 1.049, provide the date and time the exceedance occurred, the turbidity in NTU, and the date and time reported to the State. The state must be notified as soon as possible but no later than 24 hours when the CFE turbidity exceeds 1.049 NTU. (LAC 51.XII.1133.A.1) Row/Table G – Individual Filter Effluent (IFE) turbidity measurements that meet any of the following exceedance conditions must be recorded in the table. The filter number, exceedance condition, date and time the exceedance conditions occurred, the turbidity in NTU, additional actions taken, and the date and time reported to the State. (LAC 51:XII.1135.E and D) Additional Actions** required for IFE Exceedance Conditions: - For surface water systems serving a population > 10,000: - IFE turbidity > 1.049 NTU in 2 consecutive measurements taken 15 minutes apart. - Additional actions required: within 7 days of the exceedance, the system must either identify and report the obvious reason for the abnormal filter performance OR produce a filter profile for the filter and report that the profile has been produced. (LAC 51.XII.1135.E.1.a) - IFE turbidity > 0.5 NTU in 2 consecutive measurements taken 15 minutes apart at the end of the first 4 hours of continuous filter operation after the filter has been backwashed or otherwise taken off line - Additional actions: within 7 days of the exceedance, the system must either identify and report the obvious reason for the abnormal filter performance OR produce a filter profile for the filter and report that the profile has been produced. (LAC 51:XII.1135.E.1.b) - IFE turbidity > 1.049 NTU in 2 consecutive measurements taken 15 minutes apart at any time in 3 consecutive months. - Additional actions required: within 14 days of the exceedance the system shall conduct a self-assessment of the filter and report that the self-assessment was conducted. Filter self-assessment report shall include in-depth evaluation of the filter performance with historical filter turbidity data, filter profile, evaluated/identified limiting filter performance factors and corrective actions. (LAC 51:XII.1135.E.1.c) - IFE turbidity >2.049 NTU in 2 consecutive measurements taken 15 minutes apart at any time in 2 consecutive months. - Additional actions: No later than 30 days following the exceedance, the system shall arrange for the conduct of a comprehensive performance evaluation (CPE) by LDH or a third party approved by LDH and have the evaluation completed and submitted to LDH no later than 90 days following the exceedance. (LAC 51:XII.1135.E.1.c) - For surface water systems serving a population < 10,000: - IFE turbidity > 1.049 NTU in 2 consecutive measurements taken 15 minutes apart - Additional actions: the system shall report the cause or obvious reason (if known) for the exceedance. (LAC 51:XII.1135.F.1.a) - IFE turbidity > 1.049 NTU in 2 consecutive measurements taken 15 minutes apart at any time in 3 consecutive months. - Additional actions: Within 14 days of the last exceedance date, the system shall conduct a self-assessment of the filter and report that the self-assessment was conducted. (LAC 51:XII.1135.F.1.b) - IFE turbidity >2.049 NTU in 2 consecutive measurements taken 15 minutes apart at any time in 2 consecutive months. - Additional actions: No later than 60 days following the exceedance, the system shall arrange for the conduct of a CPE by LDH or a third party approved by LDH and have the evaluation completed and submitted to LDH no later than 120 days following the last exceedance. (LAC 51:XII.1135.F.1.c) **Additional Actions: 1) Filter Profile or Obvious Reason; 3) Self –Assessment of Filter; and 4) CPE

IFE and CFE turbidity must be monitored continuously and recorded every 15 minutes. CFE – - For surface water systems serving a population > 10,000 - If there is a failure in the continuous turbidity monitoring equipment, the system shall collect and analyze a CFE grab sample every 2 hours in lieu of continuous monitoring, but for no more than 5 working days following the failure of the equipment. (LAC 51:XII.1123.C) - For surface water systems serving a population < 10,000 – If there is a failure in the continuous turbidity monitoring equipment, the system shall collect and analyze a grab sample every 4 hours in lieu of continuous monitoring, but for no more than 5 working days following the failure of equipment. (LAC 51:XII.1123.C Exception) IFE – If there is a failure in the continuous turbidity monitoring equipment, the system shall conduct grab sampling every 4 hours in lieu of continuous monitoring, but for no more than 5 working days following the failure of equipment. (LAC 51:XII.1123.E.1) Disinfection Performance Criteria at Point-of-Entry to Distribution: Row/Table B - The date and duration of each instance when the disinfectant residual in water supplied to the distribution system is less than 0.5 mg/l free chlorine or 0.5 mg/l chloramine residual (measured as total chlorine) and when the LDH was notified of the occurrence. As soon as possible but no later than 24 hours from the event, the water system must notify the regional/district office that the disinfectant residual measured from any the point of entry (POE) is < 0.5 mg/l free chlorine or 0.5 mg/l chloramine residual (measured as total chlorine). The notification must include whether the disinfectant residual was restored to at least 0.5 mg/l free chlorine or 0.5 mg/l chloramine residual (measured as total chlorine) within 4 hours. (LAC 51:XII.1133.A.5)